## Pinch (hidden)
Pinch Analysis: Thermodynamic and Techno-economic HX Potential
1) List temperatures and energy of processes that need heat | [8 empty] | WW | SP | Past
| Ti (F) | To (F) | Q (MMBtu/hr) | Q (kW) |  |  |  | Q | T(F) | T(F) | T(F)
Wastewater (from wastewater boilers) | 70 | 90 | 9 | 2637.7491 |  |  |  | 0 | 70
Spray dryers | 60 | 250 | 23 | 6740.9144 |  |  |  | 9 | 90
Pastuerize | 35 | 150 | 71 | 20808.9097 |  |  |  | 0 |  | 60
Total |  |  | 103 | 30187.5733 |  |  |  | 23 |  | 250
[8 empty] | 0 |  |  | 35
2) Calculate 'Heating Composite Curve' data | [7 empty] | 71 |  |  | 150
|  | Ti | To | Qeqn | Q
|  | 35 | 60 | (60-35)/(150-35)*71 | 15.4348
|  | 60 | 70 | (70-60)/(250-60)*23+(70-60)/(150-35)*71 | 7.3844
|  | 70 | 90 | 9+(90-70)/(250-60)*23+(90-70)/(150-35)*71 | 23.7689
|  | 90 | 150 | (150-90)/(250-60)*23+(150-90)/(150-35)*71 | 44.3066
|  | 150 | 250 | (250-150)/(250-60)*23 | 12.1053
|  |  |  | total | 103
3) List temperatures and energy of processes that need cooling
| Ti | To | Q (MMBtu/hr)
Waste water | 105 | 95 | 86.875 |  | kWh/yr |  |  | x | WW | CS | Past
Cold Storage | 70 | 35 | 7.0495 | cold stor cmps | 4113391.3043 |  |  | 0 | 95
Pastuerize | 160 | 35 | 13.5115 | main ref cmps | 7884000 |  |  | 87 | 105
Total |  |  | 107.436 |  |  |  |  | 0 |  | 35
[8 empty] | 7 |  | 70
4) Calculate'Cooling Composite Curve' data | [7 empty] | 0 |  |  | 35
|  | Ti | To | Qeqn | Q |  |  | 14 |  |  | 160
|  | 70 | 35 | 7+(70-35)/(160-35)*14 | 10.92
|  | 95 | 70 | (95-70)/(160-35)*14 | 2.8
|  | 105 | 95 | (105-95)/(105-95)*87+(105-95)/(160-35)*14 | 88.12
|  | 160 | 105 | (160-105)/(160-35)*14 | 6.16
108
5) Plot heating and cooling composite curves
| dxh | dxc |  |  | x | Needs Heating | Needs Cooling
| 0 |  |  |  | 10 | 35
| 15.4348 |  |  |  | 25.4348 | 60
| 7.3844 |  |  |  | 32.8192 | 70
| 23.7689 |  |  |  | 56.5881 | 90
| 44.3066 |  |  |  | 100.8947 | 150
| 12.1053 |  |  |  | 113 | 250
|  | 0 |  |  | 10 |  | 35
|  | 10.92 |  |  | 20.92 |  | 70
|  | 2.8 |  |  | 23.72 |  | 95
|  | 88.12 |  |  | 111.84 |  | 105
|  | 6.16 |  |  | 118 |  | 160
6) Shift cooling curve until minimum pinch = 10 F
x0 | dxh | dxc |  |  | x | Needs Heating | Needs Cooling
| 0 |  |  |  | 65 | 35
| 15.4348 |  |  |  | 80.4348 | 60
| 7.3844 |  |  |  | 87.8192 | 70
| 23.7689 |  |  |  | 111.5881 | 90
| 44.3066 |  |  |  | 155.8947 | 150
| 12.1053 |  |  |  | 168 | 250
|  | 0 |  |  | 10 |  | 35
|  | 10.92 |  |  | 20.92 |  | 70
|  | 2.8 |  |  | 23.72 |  | 95
|  | 88.12 |  |  | 111.84 |  | 105
|  | 6.16 |  |  | 118 |  | 160
7) Overlap is thermodynamically possible H/C savings by employing HXs
Input Data | [5 empty] | 87
Ql | 64 |  |  |  |  | 0.84466
Qh | 118 |  |  |  |  | 0.81308 | [5 empty] | Total 68,080 MMBTU biogas produced in 2020.40% flared out, 60% used in boiler. We are working on projects to send >90% to boiler.
Qnc | 107 | [10 empty] | 40% flared out, 60% used in boiler. We are working on projects to send >90% to boiler.
Qnh | 103 | [10 empty] | Working on projects to send >90% to boiler.
Calcs
Qhx = Qh-Qh (MMBtu/hr) | 54
Qhx/Qnc | 50.47%
Qhx/Qnh | 52.43%
In this case 116-29=87 MMBtu/hr 87/103 =84%ofheat 87/107 =81%ofcool
8) Determine actual techno/economic HX savings
9) Determine ratio of techno-economically feasible / thermodynamically feasible savings
9) Employ heat pumps to use remainin cooling energy as heat source for remaining heating
10) Employ electric resistance, other hps, or biogas for remaining high temp heat requirements
| dx | y | y
| Q | Ti | To
| 10.92 | 70 | 35
| 2.8 | 95 | 70
| 88.12 | 105 | 95
| 6.16 | 160 | 105
dx
| Q | x | y
| 0 | 10 | 35
| 10.92 | 20.92 | 70
| 2.8 | 23.72 | 95
| 88.12 | 111.84 | 105
| 6.16 | 118 | 160
Biogas
'Pinch'
=10 F
HPs

## Streams
Stream No. | Stream Name | Tin | Tout | Q | Stream Type
|  | °F | °F | MMBtu/hr
1 | Hot Water | 55 | 130 | 11.98 | Needs Heating
2 | Scalding Water | 179 | 188 | 1.75 | Needs Heating
3 | Compressor Oil | 170 | 130 | 0.6 | Needs Cooling
4 | Ammonia Desuperheating | 170 | 94.4768 | 2.11 | Needs Cooling
5 | Ammonia Condensing | 94.4768 | 94.4768 | 21.77 | Needs Cooling
6 | Waste-Water | 75 | 50 | 8.67 | Needs Cooling

## Sheet3 (hidden)
Tin | Tout | mCp | Q
°F | °F | MMBtu/°F-hr | MMBtu/hr
°C | °C | kJ/°C-hr | kJ/hr
|  | kW/°C | kW
|  | MW/°C | MW
|  | MJ/°C-hr | MJ/hr

## Sheet2 (hidden)
Needs Heating
Needs Cooling